BILCO Type FT-30 flood tight floor access doors are constructed for use in applications where there is concern of water or other liquids entering the access opening. Type FT-30 doors are rated to withstand a 30-foot (9.14m) head of water from the topside without leakage and up to a 5-foot (1.52m) head of water from the underside (when specified) and will resist low-pressure gases and odors. Doors are reinforced for AASHTO H-20 wheel loading and feature aluminum construction, type 316 stainless steel hardware, and engineered lift assistance for easy one-hand operation. Products are available in a number of standard sizes and special sizes can be specified. For more information, please visit our website www.bilco.com or call 1-800-366-6530.

SECTION 083100

Flood tight Floor access DOORS

(BILCO TYPE FT-30)

- GENERAL

      - SUMMARY

        - Work Included:  Provide factory-fabricated floor access doors.

      - SUBMITTALS

        - Product Data:  Submit manufacturer’s product data.

        - Shop Drawings: Submit shop drawings including profiles, accessories, location, adjacent construction interface, and dimensions.

        - Warranty:  Submit executed copy of manufacturer’s standard warranty.

      - QUALITY ASSURANCE

        - Manufacturer:  A minimum of 5 years experience manufacturing similar products.

        - Installer:  A minimum of 2 years experience installing similar products.

        - Manufacturer’s Quality System: Registered to ISO 9001 Quality Standards including in-house engineering for product design activities.

      - DELIVERY, STORAGE AND HANDLING

        - Deliver products in manufacturer’s original packaging.  Store materials in a dry, protected, well-vented area. Inspect product upon receipt and report damaged material immediately to delivering carrier and note such damage on the carrier’s freight bill of lading.

      - WARRANTY

        - Manufacturer’s Warranty:  Provide manufacturer’s standard warranty.  Materials shall be free of defects in material and workmanship for a period of twenty-five years from the date of purchase. Should a part fail to function in normal use within this period, manufacturer shall furnish a new part at no charge.

- PRODUCTS

      - manufacturer

        - Basis-of-Design Manufacturer:  Type FT-30 Flood Tight Access Door by The BILCO Company, P.O. Box 1203, New Haven, CT 06505, 1-800-366-6530, Fax: 1-203-535-1582, Web: www.bilco.com.

      - ACCESS DOOR

        - Furnish and install where indicated on plans vault access door Type FT-30, size [insert: width (_____) x length (_____)]. Length denotes hinge side. The floor access door shall be single leaf and pre-assembled from the manufacturer.

        - Performance characteristics:

          - Doors are rated to withstand a 30-foot (9.14m) head of water from the topside without leakage and up to a 5-foot (1.52m) head of water from the underside (when specified) and will resist low-pressure gases and odors.

          - Cover: Shall be reinforced to support AASHTO H-20 wheel load with a maximum deflection of 1/150th of the span. Manufacturer to provide structural calculations stamped by a registered professional engineer upon request. (Note: For installation in an off-street location where not subject to high-density, fast-moving traffic.)

          - Operation of the cover shall be smooth and easy with controlled operation

          - Operation of the cover shall not be affected by temperature.

          - Entire door, including all hardware components, shall be highly corrosion resistant.

        - Cover: Shall be 1/4” (6mm) aluminum diamond pattern [insert: Thermion Safetrax with a coefficient of friction of 1.1 for a non-skid cover finish).

        - Frame: Extruded aluminum with bend down anchor tabs around the perimeter. Extrusion is designed with a water retention lip to keep standing water from falling into the opening.

        - Hinges: Shall be specifically designed for horizontal installation and shall be welded to the cover and the frame.

        - Lifting mechanisms: Manufacturer shall provide the required combination of stainless-steel gas charged lifting mechanisms.

        - Gasket: Shall be a “D” profile adhesive bonded EPDM gasket around the entire perimeter of the cover.

        - Hardware:

          - Hinges: Full length formed aluminum piano hinge with a type 316 stainless steel pin.

          - Cover shall be equipped with a hold open device that automatically locks the cover in the open position.

          - Cover shall be fitted with the required combination of stainless-steel gas springs.

          - Each door will be equipped with a minimum of 2 lever type lock assemblies to compress the gasket to provide a flood tight seal. Each lock is engaged by turning a hex head bolt from the topside of the door.

          - Hardware: Shall be Type 316 stainless steel throughout.

        - Finishes: Factory finish shall be mill finish aluminum with bituminous coating applied to the exterior of the frame.

- EXECUTION

      - EXAMINATION

        - Examine substrates and openings for compliance with requirements for installation tolerances and other conditions affecting performance.  Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

        - Install products in strict accordance with manufacturer’s instructions and approved submittals.  Locate units level, plumb, and in proper alignment with adjacent work.

          - Test units for proper function and adjust until proper operation is achieved.

          - Repair finishes damaged during installation.

          - Restore finishes so no evidence remains of corrective work.

      - ADJUSTING AND CLEANING

        - Clean exposed surfaces using methods acceptable to the manufacturer which will not damage finish.

        - Gasket and gasket sealing surface should be cleaned and free of debris to maintain watertight seal.

END OF SECTION